## AssetList (hidden)
Assets | Age | 0-30, 31-50, >51, Unknown | Age | 0-20, 21-30, >31, Unknown | Material | Size
Aerator | 0 | 0-30 | 0 | 0-20 | Asbestos Cement | 3/4"
Alarm System | 31 | 31-50 | 21 | 21-30 | Cast Iron | 1"
Backflow Prevention Device | 51 | >51 | 31 | >31 | Concrete | 1.5"
Backwash Tank | Unknown | Unknown | Unknown | Unknown | Copper | 2"
Blower |  |  |  |  | Ductile Iron | 2.5"
Chemical Equipment |  |  |  |  | Galvanized | 3"
Computer |  |  |  |  | HDPE | 4"
Control Panel |  |  |  |  | Lead | 5"
Curb Stop |  |  |  |  | Other | 6"
Dehumidifier |  |  |  |  | PEX | 8"
Detention Tank |  |  |  |  | Polyethylene | 10"
Distribution Line/Watermain |  |  |  |  | PVC | 12"
Electrical Equipment |  |  |  |  | Steel | 14"
Filter - Concrete |  |  |  |  | Unknown | 16"
Filter - Metal | [5 empty] | Unknown
Filter Media
Gas Detection Equipment
Generator
Heater - Electric
Heater - Furnace
Hydrant - Fire
Hydrant - Flushing
Laboratory Equipment
Land
Mechanical Equipment
Membrane Treatment
Meter
Meter Reading Equipment
Miscellaneous Project Costs
Other Water Treatment
Pump
Service Line
Softener
Storage Tank - Bladder
Storage Tank - Hydropneumatic
Storage Tank - Plastic
Storage Tank - Tower, ground, standpipe
Storage Tank Interior/Exterior Paint
Structure - Block
Structure - Steel Frame
Structure - Stick Built
Valve
Well

## Title Page
City of
Asset Management
Water System
Prepared by: Minnesota Rural Water Association
2023
Template Version: 10/2023

## Intro
Asset Management Guidance for Water and Wastewater Systems
Asset Management Definition
An asset management plan is a focused plan to manage the public water system assets that are needed to provide
a safe, reliable drinking water supply now and into the future. It is more than just a list of water system
assets and their locations. It should include all aspects of a drinking water system including source,
treatment, storage, and distribution. The plan should assess each component from both a technical and
financial aspect to determine the most cost effective approach for the desired level of service. An asset
management plan includes a strategy for asset replacement utilizing the useful life and criticality of the assets.
The asset management plan is a guide designed to lead to a fiscally sustainable water system by determining
annual operations and maintenance needs as well as planning for future capital investments.
The Five Core Components of Asset Management
1. Assets – This involves making a complete list of all assets in the system. For each asset, include
as much information as possible in the document including name brand, serial and model
numbers, size of pumps, horsepower of motors, any notes on replacement or maintenance on the
asset, or any other information that is important to note about the asset. The Condition is a
description of the current age and level of preventative maintenance performed on the asset.
Include addresses for all assets. A parcel code can be used for locations without a physical
address. Taking pictures of each asset may be helpful in keeping track of multiple assets. Items
to consider when making a list of your assets:
|  | i. | What do you own?
|  | ii. | Where are the assets located?
|  | iii. | What is the condition?
|  | iv. | What is the remaining useful life?
|  | v. | What is the value?
2. Service Level – The level of service establishes what your utility wants your assets to provide.
In addition, it outlines your goals in order to provide your customers what they want from your
utility. The goals can be in several areas such as water loss, water quality and should be "SMART"
(specific, measurable, attainable, realistic or relevant, and time bound). For example, "The water
utility will provide water at a minimum pressure of 50 psi 95% of the time." This goal is specific
as it states very clearly what the utility is trying to accomplish. This goal is measurable as the
pressure can be checked throughout the distribution system. This goal is attainable if the utility
has proper storage and pumping facilities to meet that pressure level. This goal is realistic as it
is at a level that customers would want the utility to maintain. Finally, this goal is time bound by
stating that the pressure will be met 95% of the time. This allows for time periods when the
system is down for repairs when the pressure may drop below 50 psi. It is a good idea to review and
measure how the utility is meeting the goals periodically and to report the results to the public
or decision-makers with the utility at least annually. Items to consider when discussing service
level:
|  | i. | What do your customers want?
|  | ii. | What are your customers willing to pay?
|  | iii. | What are you able to provide?
|  | iv. | How will you measure your performance?
3. Criticality - The Criticality Analysis Rating is a description of how critical an asset is to the
water and wastewater system. Items to consider when deciding on the criticality include the
likelihood of failure and the consequence if the asset fails. It is important to remember that
some assets are more critical than others in the system. Those assets that are more critical
should be the focus of the utility staff and money.
|  | i. | What is the probability of failure?
|  | ii. | What is the consequence of failure?
|  | iii. | Do you have backup equipment?
|  | iv. | Can you increase energy efficiency?
4. Life Cycle –The utility will need to make decisions as to how they will operate and maintain
their assets including deciding when to continue to repair an asset and when to replace it.
Typically, by spending more on routine maintenance means spending less on replacement.
Generally speaking, routine maintenance is cheaper than replacing assets. Utilities will need to
evaluate how much time and money is devoted to routine maintenance and that will involve
thinking about the criticality of the assets. More routine maintenance should be performed on
the highly critical assets than those that are less critical.
|  | i. | What is the life expectancy of your assets?
|  | ii. | What are the operation and maintenance costs?
|  | iii. | What will it cost to replace them?
|  | iv. | How do you know when to repair or rehabilitate and when to replace?
5. Funding – The utility managers will need to decide how much money is needed for operations,
routine maintenance and replacement of assets. Communication is extremely important between
both the decision makers and operations staff when discussing funding.
|  | i. | Where will you get the money for operation and maintenance?
|  | ii. | Where will you get the money for asset replacement?
|  | iii. | Where will you get the money for increasing energy efficiency?
Using the Template
Asset Management Instructions are available at: |  |  |  | www.mrwa.com
Each template is designed so that the first page titled Water System Inventory (or Wastewater System
Inventory) is a summary of assets and dollar amounts that are entered into the document for all assets. All
dollar amounts that are entered into the document will automatically appear on the Inventory. At the bottom
of the Inventory page is a Criticality Analysis Rating and Condition. When the Year Installed is entered into
the cells the document will automatically calculate the Replacement Date and Remaining Life for each asset.
When the Original Cost is entered into the cells, the document will automatically calculate the Current Value
and Annual Depreciation for each asset. At the back of the Asset Management document is space for any
maintenance records to be entered. It is important to enter as much information into the template as possible
about your assets. Also, assets change over time so it is important to review and update the asset inventory
on an annual basis.
DO NOT fill in the yellow columns of data in the Data Tab. You will destroy the formulas and data integrity
Sources
Asset Management Guidance for Water Systems, Michigan Department of Environmental Quality
July 2013, Accessed June 28, 2016
Asset Management: A Handbook for Small Water Systems, United States Environmental Protection Agency,
www.epa.gov
September 2003, Accessed June 28, 2016
Asset Management - The Five Core Components, Southwest Environmental Finance Center, May 12, 2016.
An Introduction to Asset Management and Asset Management Resources, Southwest Environmental
Finance Center, May 12, 2016.

## Service Line Inventory
Service Line Inventory
On December 16, 2021, the Environmental Protection Agency (EPA) announced that the current Lead and
Copper Rule Revisions (LCRR), originally published on January 15, 2021, at Federal Register, 86 FR 4198 will
go into effect to support development of actions to reduce lead in drinking water. EPA directed states and
systems to prioritize developing lead service line inventories which will need to be submitted by the
compliance date October 16, 2024.
The Lead and Copper Rule Revisions require public water systems to identify the service line materials of all
service line connections in their distribution system regardless of ownership status. The rule determines the
minimum information required to be needed in your lead service line (LSL) inventory, how to communicate
about your system inventory, and how often to update the inventory. It may be more useful to the system
while conducting their inventory to gather additional or more detailed information than required.
The service lines in a drinking water system are assets and should be included in an asset management plan.
The Minnesota Department of Health has information available on their website to assist public water
systems in completing their service line inventory. Information on identifying service lines, lead service line
replacement, and lead service line inventory technical assistance can be found on the Lead and Copper Rule
Revisions webpage.
Lead and Copper Rule Revisions For Minnesota Public Water Systems - MN Dept. of Health (state.mn.us)
Additionally, the Minnesota Department of Health has service line inventory templates available on the
webpage. There are templates for single ownership and split ownership. The templates are available in both
"simple" and "detailed" versions and include instructions for both templates. The "simple" version is the
minimum required and the "detailed" version is suggested. As mentioned above, the service line inventory
must be completed and submitted to the Minnesota Department of Health by October 16, 2024.
Any questions on the Lead and Copper Rule Revisions, including instruction, questions or for assistance in
completing the service line inventory, please contact the Minnesota Rural Water Association Lead and
Copper Technical Advisor at 800-367-6792 or the Minnesota Department of Health at 651-201-4700.

## Data
STOP & READ: You CAN NOT enter data over the yellow cells or you will destroy the formulas and data integrity.
Distribution Information
Infrastructure Type | Assets | Useful Life | Item | Size (" Indicator Required) | Length (Only Enter Value) | Material | Location | Condition | Year Installed | Replacement Date | % of Life Used | Remaining Life | Original Cost | Current Value | Annual Depreciation | Criticality Analysis (1-25) | Comments | Age (yrs) | 0-30, 31-50->51, Unknown | 0-10, 11-20, > 21, Unknown
Distribution | Distribution Line/Watermain | 1 | 1650' of 8" C900 (EXAMPLE DATA) | 8" | 1650 | PVC | Main Street | Replace | 2017 | 2018 | 100% | 0 | 168300 | 0 | 0 | 1 |  | 6 | 0-30 | 0-20
Source | Well | 60 | Well #2 (Unique #409994) (EXAMPLE DATA) |  |  |  | 200 First Avenue | Fair | 1983 | 2043 | 66.67% | 20 |  | 0 | 0 | 20 |  | 40 | 31-50 | >31
Source | Pump | 10 | Well #1 submersible pump - 7HP (EXAMPLE DATA) |  |  |  | 200 First Avenue | Good | 2020 | 2030 | 30% | 7 |  | 0 | 0 | 12 |  | 3 | 0-30 | 0-20
Source | Electrical Equipment | 40 | Well #1 Control Box (EXAMPLE DATA) |  |  |  | 200 First Avenue | Replace | 1982 | 2022 | 100% | 0 | 0 | 0 | 0 | 17 |  | 41 | 31-50 | >31
Treatment | Chemical Equipment | 12 | Blue-White Industries Peristaltic Chlorine Pump (EXAMPLE DATA) |  |  |  | 200 First Avenue | NA |  | 12 | 100% | 0 | 2351.5 | 0 | 0 | 5 |  | 2023 | >51 | >31
Storage | Storage Tank - Tower, ground, standpipe | 70 | 50,000 gallon Water Tower (EXAMPLE DATA) |  |  |  | 700 Maple Street | Excellent | 2023 | 2093 | 0% | 70 | 1160400 | 1160400 | 16577.1429 | 1 |  | 0 | 0-30 | 0-20
Distribution | Valve |  | 6" Isolation Valve (Hydrant 1) (#1) (EXAMPLE DATA) | 6" |  |  | Main Street & Maple Street | NA | 2022 | 2022 | NA | 0 | 1900 | 0 | 0 | 1 |  | 1 | 0-30 | 0-20
Distribution | Valve |  | 6" Isolation Valve (Hydrant 1) (#1) (EXAMPLE DATA) | Unknown |  |  |  | NA |  | 0 | NA | 0 |  | 0 | 0 |  |  | 2023 | >51 | >31
Distribution | Hydrant - Fire | 60 | 1 (EXAMPLE DATA) |  |  |  | Main Street & Maple Street | Excellent | 2022 | 2082 | 1.667% | 59 | 6600 | 6490 | 110 | 1 |  | 1 | 0-30 | 0-20
Distribution | Meter | 25 | 999100SC (EXAMPLE DATA) | 3/4" |  |  | 500 Oak Avenue | Fair | 2003 | 2028 | 80% | 5 | 193 | 38.6 | 7.72 | 9 |  | 20 | 0-30 | 0-20
Distribution | Curb Stop | 50 | (EXAMPLE DATA) | 1" |  |  | 500 Oak Avenue | Excellent | 2022 | 2072 | 2% | 49 | 700 | 686 | 14 | 1 |  | 1 | 0-30 | 0-20
Formulas:
Current Value = IFERROR(IF(Table6[[#This Row],[Year Installed]]>YEAR(TODAY()),Table6[[#This Row],[Original Cost]],(Table6[[#This Row],[Original Cost]]/Table6[[#This Row],[Useful Life]])*Table6[[#This Row],[Remaining Life]]),0)

## Comments
Comments:

## Water System Inventory
| Current Year: | 2023
Infrastructure Type | Assets | Original Cost | Current Value | Annual Depreciation
Distribution | Distribution Line/Watermain | 168300 | 0 | 0
Distribution | Valve | 1900 | 0 | 0
Distribution | Meter | 193 | 38.6 | 7.72
Distribution | Hydrant - Fire | 6600 | 6490 | 110
Distribution | Curb Stop | 700 | 686 | 14
Distribution Total |  | 177693 | 7214.6 | 131.72
Storage | Storage Tank - Tower, ground, standpipe | 1160400 | 1160400 | 16577.1429
Storage Total |  | 1160400 | 1160400 | 16577.1429
Treatment | Chemical Equipment | 2351.5 | 0 | 0
Treatment Total |  | 2351.5 | 0 | 0
Source | Electrical Equipment | 0 | 0 | 0
Source | Well |  | 0 | 0
Source | Pump |  | 0 | 0
Source Total |  | 0 | 0 | 0
Total Assets/Annual Depreciation |  | 1340444.5 | 1167614.6 | 16708.8629

## Source
Infrastructure Type | Assets | Useful Life | Item | Location | Condition | Year Installed | Replacement Date | Remaining Life | Annual Depreciation | Criticality Analysis (1-25) | Original Cost | Current Value
Source | Electrical Equipment | 40 | Well #1 Control Box (EXAMPLE DATA) | 200 First Avenue | Replace | 1982 | 2022 | 0 | 0 | 17 | 0 | 0
Source | Electrical Equipment Total | [9 empty] | 0 | 0
Source | Well | 60 | Well #2 (Unique #409994) (EXAMPLE DATA) | 200 First Avenue | Fair | 1983 | 2043 | 20 | 0 | 20 | 0 | 0
Source | Well Total | [9 empty] | 0 | 0
Source | Pump | 10 | Well #1 submersible pump - 7HP (EXAMPLE DATA) | 200 First Avenue | Good | 2020 | 2030 | 7 | 0 | 12 | 0 | 0
Source | Pump Total | [9 empty] | 0 | 0
Grand Total | [10 empty] | 0 | 0

## Treatment
Infrastructure Type | Assets | Useful Life | Item | Location | Condition | Year Installed | Replacement Date | Remaining Life | Annual Depreciation | Criticality Analysis (1-25) | Original Cost | Current Value
Treatment | Chemical Equipment | 12 | Blue-White Industries Peristaltic Chlorine Pump (EXAMPLE DATA) | 200 First Avenue | NA | (blank) | 12 | 0 | 0 | 5 | 2351.5 | 0
Treatment | Chemical Equipment Total | [9 empty] | 2351.5 | 0
Grand Total | [10 empty] | 2351.5 | 0

## Storage
Infrastructure Type | Assets | Useful Life | Item | Location | Condition | Year Installed | Replacement Date | Remaining Life | Annual Depreciation | Criticality Analysis (1-25) | Original Cost | Current Value
Storage | Storage Tank - Tower, ground, standpipe | 70 | 50,000 gallon Water Tower (EXAMPLE DATA) | 700 Maple Street | Excellent | 2023 | 2093 | 70 | 16577.1429 | 1 | 1160400 | 1160400
Storage | Storage Tank - Tower, ground, standpipe Total | [9 empty] | 1160400 | 1160400
Grand Total | [10 empty] | 1160400 | 1160400

## Distribution
Infrastructure Type | Assets | Useful Life | Item | Location | Condition | Year Installed | Replacement Date | Remaining Life | Annual Depreciation | Criticality Analysis (1-25) | Original Cost | Current Value
Distribution | Distribution Line/Watermain | 1 | 1650' of 8" C900 (EXAMPLE DATA) | Main Street | Replace | 2017 | 2018 | 0 | 0 | 1 | 168300 | 0
Distribution | Distribution Line/Watermain Total | [9 empty] | 168300 | 0
Distribution | Valve | (blank) | 6" Isolation Valve (Hydrant 1) (#1) (EXAMPLE DATA) | Main Street & Maple Street | NA | 2022 | 2022 | 0 | 0 | 1 | 1900 | 0
Distribution | Valve | (blank) | 6" Isolation Valve (Hydrant 1) (#1) (EXAMPLE DATA) | (blank) | NA | (blank) | 0 | 0 | 0 | (blank) | 0 | 0
Distribution | Valve Total | [9 empty] | 1900 | 0
Distribution | Meter | 25 | 999100SC (EXAMPLE DATA) | 500 Oak Avenue | Fair | 2003 | 2028 | 5 | 7.72 | 9 | 193 | 38.6
Distribution | Meter Total | [9 empty] | 193 | 38.6
Distribution | Hydrant - Fire | 60 | 1 (EXAMPLE DATA) | Main Street & Maple Street | Excellent | 2022 | 2082 | 59 | 110 | 1 | 6600 | 6490
Distribution | Hydrant - Fire Total | [9 empty] | 6600 | 6490
Distribution | Curb Stop | 50 | (EXAMPLE DATA) | 500 Oak Avenue | Excellent | 2022 | 2072 | 49 | 14 | 1 | 700 | 686
Distribution | Curb Stop Total | [9 empty] | 700 | 686
Grand Total | [10 empty] | 177693 | 7214.6

## Meters
Meters
System Name | PWS ID | Data Entry Date
0 | 0 | 0
Infrastructure Type | Distribution
Assets | Meter |  | Note: For the pivot table to work correctly,
Box 5B must be filtered to meters only
Size - in | Age | How Many
3/4" | 0-20 | 1
Grand Total |  | 1

## Hydrants
Hydrants
System Name | PWS ID | Data Entry Date
0 | 0 | 0
Infrastructure Type | Distribution
Assets | Hydrant - Fire |  | Note: For the pivot table to work correctly,
Box 5B must be filtered to Hydrant-Fire only
Age - Yrs | How many
0-30 | 1
Grand Total | 1

## Valves
Valves
System Name | PWS ID | Data Entry Date
0 | 0 | 0
Infrastructure Type | Distribution
Assets | Valve |  | Note: For the pivot table to work correctly,
Box 5B must be filtered to Valves only
Size - in | Age - Yrs | How Many
6" | 0-30 | 1
Unknown | >51 | 1
Grand Total |  | 2

## Dist Line Watermain
Watermain/Distribution Lines
System Name |  | PWS ID | Data Entry Date
Infrastructure Type | Distribution |  |  | Note: For the pivot table to work correctly,
Assets | Distribution Line/Watermain |  |  | Box 5B must be filtered to
Distribution Line/Watermain only
Size - in | Age - Yrs | Material | Total Length
8" | 0-30 | PVC | 1650
Grand Total |  |  | 1650

## Overall Condition
Condition | Count of Condition | Percentage
Excellent | 3 | 27.27%
Fair | 2 | 18.18%
Good | 1 | 9.091%
NA | 3 | 27.27%
Replace | 2 | 18.18%
Grand Total | 11 | 100%

## Asset Graphs
Condition |  | Condition
Infrastructure Type | Assets | Good | Fair | Excellent | Replace | NA | Grand Total
Distribution | Distribution Line/Watermain |  |  |  | 1 |  | 1
| Valve |  |  |  |  | 2 | 2
| Meter |  | 1 |  |  |  | 1
| Hydrant - Fire |  |  | 1 |  |  | 1
| Curb Stop |  |  | 1 |  |  | 1
Storage | Storage Tank - Tower, ground, standpipe |  |  | 1 |  |  | 1
Treatment | Chemical Equipment |  |  |  |  | 1 | 1
Source | Electrical Equipment |  |  |  | 1 |  | 1
| Well |  | 1 |  |  |  | 1
| Pump | 1 |  |  |  |  | 1
Grand Total |  | 1 | 2 | 3 | 2 | 3 | 11
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Hydrant Maintenance
Fire Hydrant Maintenance
Item | Approximate Address Location | Year Installed | Make | Hydrant Gate Valve Yes/No | Maintenance
Insert additional line here

## Historical Costs
Historical Costs
*ESTIMATED HISTORICAL COSTS
YEAR | 3/4" Meter | 1" Meter | 4" C900 PVC Pipe/Ft | 6" C900 PVC Pipe/Ft | 8" C900 PVC Pipe/Ft | 10" C900 PVC Pipe/Ft
2022 | 300 | 350 | 25 | 30 | 40 | 50
2016 | 260 | 280 | 17 | 20 | 35 | 45
2011 | 233 | 250.88 | 15.232 | 17.92 | 31.36 | 40.32
2006 | 208 | 223.72 | 13.583 | 15.98 | 27.965 | 35.955
2001 | 183 | 196.56 | 11.934 | 14.04 | 24.57 | 31.59
1996 | 157 | 169.4 | 10.285 | 12.1 | 21.175 | 27.225
1991 | 132 | 142.24 | 8.636 | 10.16 | 17.78 | 22.86
1986 | 107 | 115.08 | 6.987 | 8.22 | 14.385 | 18.495
1981 | 82 | 87.92 | 5.338 | 6.28 | 10.99 | 14.13
1976 | 56 | 60.76 | 3.689 | 4.34 | 7.595 | 9.765
YEAR | 4" Ductile Iron Pipe/Ft | 6" Ductile Iron Pipe/Ft | 8" Ductile Iron Pipe/Ft | 10" Ductile Iron Pipe/Ft | 1" Curb Stop/Riser | 1" Copper Service Line/ft
2022 | 46 | 38 | 53 | 61 | 700 | 47
2016 | 40 | 29 | 45 | 53 | 500 | 37.6
2011 | 35.84 | 25.984 | 40.32 | 47.488 | 448 | 33.6896
2006 | 31.96 | 23.171 | 35.955 | 42.347 | 400 | 30.0424
2001 | 28.08 | 20.358 | 31.59 | 37.206 | 351 | 26.3952
1996 | 24.2 | 17.545 | 27.225 | 32.065 | 303 | 22.748
1991 | 20.32 | 14.732 | 22.86 | 26.924 | 254 | 19.1008
1986 | 16.44 | 11.919 | 18.495 | 21.783 | 205.5 | 15.4536
1981 | 12.56 | 9.106 | 14.13 | 16.642 | 157 | 11.8064
1976 | 8.68 | 6.293 | 9.765 | 11.501 | 108.5 | 8.1592
YEAR | 4" Valve & Valve Box | 6" Valve & Valve Box | 8" Valve & Valve Box | 10" Valve & Valve Box | Hydrant - Fire | Hydant - Flushing
2022 | 1800 | 2250 | 3000 | 3500 | 6600 | 2700
2016 | 1233 | 2000 | 2360 | 2800 | 4600 | 2100
2011 | 1104.768 | 1792 | 2114.56 | 2508.8 | 4121.6 | 1881.6
2006 | 985.167 | 1598 | 1885.64 | 2237.2 | 3675.4 | 1677.9
2001 | 865.566 | 1404 | 1656.72 | 1965.6 | 3229.2 | 1474.2
1996 | 745.965 | 1210 | 1427.8 | 1694 | 2783 | 1270.5
1991 | 626.364 | 1016 | 1198.88 | 1422.4 | 2336.8 | 1066.8
1986 | 506.763 | 822 | 969.96 | 1150.8 | 1890.6 | 863.1
1981 | 387.162 | 628 | 741.04 | 879.2 | 1444.4 | 659.4
1976 | 267.561 | 434 | 512.12 | 607.6 | 998.2 | 455.7
High Density Poly-Ethylene
YEAR | 2" HDPE Pipe/Ft | 4" HDPE Pipe/Ft | 6" HDPE Pipe/Ft | 8" HDPE Pipe/Ft | 10" HDPE Pipe/Ft | 12" HDPE Pipe/Ft
2022 | 50 | 75 | 90 | 105 | 115 | 140
2016 | 40 | 60 | 72 | 84 | 92 | 112
2011 | 35.84 | 53.76 | 64.512 | 75.264 | 82.432 | 100.352
2006 | 31.96 | 47.94 | 57.528 | 67.116 | 73.508 | 89.488
2001 | 28.08 | 42.12 | 50.544 | 58.968 | 64.584 | 78.624
1996 | 24.2 | 36.3 | 43.56 | 50.82 | 55.66 | 67.76
1991 | 20.32 | 30.48 | 36.576 | 42.672 | 46.736 | 56.896
1986 | 16.44 | 24.66 | 29.592 | 34.524 | 37.812 | 46.032
1981 | 12.56 | 18.84 | 22.608 | 26.376 | 28.888 | 35.168
1976 | 8.68 | 13.02 | 15.624 | 18.228 | 19.964 | 24.304
YEAR | 14" HDPE Pipe/Ft | 16" HDPE Pipe/Ft | PEP Coiled Plastic Pipe 3/4"/Ft | PEP Coiled Plastic Pipe 1"/Ft | PEP Coiled Plastic Pipe 1.5"/Ft | PEP Coiled Plastic Pipe 2"/Ft
2022 | 180 | 220 | 40.4 | 40.79 | 41.7 | 42.5
2016 | 144 | 176 | 32.32 | 32.63 | 33.36 | 34
2011 | 129.024 | 157.696 | 28.9587 | 29.2365 | 29.8906 | 30.464
2006 | 115.056 | 140.624 | 25.8237 | 26.0714 | 26.6546 | 27.166
2001 | 101.088 | 123.552 | 22.6886 | 22.9063 | 23.4187 | 23.868
1996 | 87.12 | 106.48 | 19.5536 | 19.7412 | 20.1828 | 20.57
1991 | 73.152 | 89.408 | 16.4186 | 16.576 | 16.9469 | 17.272
1986 | 59.184 | 72.336 | 13.2835 | 13.4109 | 13.711 | 13.974
1981 | 45.216 | 55.264 | 10.1485 | 10.2458 | 10.475 | 10.676
1976 | 31.248 | 38.192 | 7.0134 | 7.0807 | 7.2391 | 7.378
*If you are unable to locate the original costs of your asset, you can use this table of data as a general reference. These estimated values are intended to represent both materials and standard installation costs.

## Asset Rating
Asset
Date
Consequence | 5 | 5 | 10 | 15 | 20 | 25
(Cost) of Failure | 4 | 4 | 8 | 12 | 16 | 20
| 3 | 3 | 6 | 9 | 12 | 15
| 2 | 2 | 4 | 6 | 8 | 10
| 1 | 1 | 2 | 3 | 4 | 5
Multiplied By |  | 1 | 2 | 3 | 4 | 5
Probability of Failure
1 Very Low 2 Low 3 Moderate 4 High 5 Very High
(1-2) (3-4) | (5-8) |  | (9-12) |  | (15-25)
To use this table, estimate the probability of failure from 1 to 5, with 5 being very high probability of failure
and 1 being a very low probability of failure. Then assess the consequence of failure from 1 to 5 in the same
manner. Using the number of probability of failure, move across the row until the column associated with
the number for consequences of failure is reached. Alternatively, move down the column for the
consequence of failure until the row for probability of failure is reached. Locate the number that is in the box
where the row and column intersect. That is the criticality number for the asset.
As an example in a water system:
Asset: Pine Street water main; constructed in 1950
Service History: One service repair in the past 15 years.
Probability of failure: 3 - the water main is old, and will most likely need to be replaced in the next 10 years,
but is still in reasonable condition.
Consequence of failure: 2 - the water main services a now-abandoned industrial park. The city wants to
maintain the service but presently serves no customers. The water main has easy access, so repair is
relatively easy and timely.
Probability of failure * Consequence of failure = Criticality Factor 3 * 2 = 6
Criticality Factor: 6 - A 6 would not be considered a critical rating. Typically an asset falling in the criticality
range of 1 to 8 will not be considered critical. An asset falling in the criticality range of 9 to 15 will be important,
but not critical. An asset above 16 in the criticality range will be considered critical.
Use one form for each asset

## Asset Condition
Condition Rating System Using Remaining Life
Condition | Description
Excellent | New, less than 20% of useful life used up. Requires only minimal preventative maintenance to maintain proper function. Meets all operational, functional, obvious safety and regulatory requirements.
Good | Between 21% and 60% of useful life used up. Requires average level of preventative maintenance and may require minimal corrective maintenance or minor adjustments to optimize performance.
Fair | Between 61% and 85% of useful life used up. Requires significant reactive maintenance and/or partial refurbishment/replacement to restore it to good condition.
Poor | Between 86% and 100% of useful life used up, needs to be replaced. Operational but requires significant, timely refurbishment to avoid further deterioration and/or failure. Rehabilitate or replace if possible.
Replace | Needs to be replaced. Asset is in obsolete/replacement required condition. It is generally past cost effective refurbishment and needs to be replaced.

## Rating (hidden)
[9 empty] | Current Year |  |  | 2023
Condition Rating System Using Remaining Life Range
Useful Life | Excellent | Excellent | Less than 20% | Good | Good | 21-60% | Fair | Fair | 61-85% | Poor | Poor | 86-100% | 0-20% | Excellent
in Years | Less than 20% |  | Year | 21-60% |  | Year | 61-85% |  | Year | 86-100% |  | Year | 21-60% | Good
5 | 1 | Newer than | 2022 | 3 | to | 2020 | 4.25 | to | 2019 | 5 | to | 2018 | 61-85% | Fair
10 | 2 | Newer than | 2021 | 6 | to | 2017 | 8.5 | to | 2015 | 10 | to | 2013 | 86-99% | Poor
15 | 3 | Newer than | 2020 | 9 | to | 2014 | 12.75 | to | 2010 | 15 | to | 2008 | 100% | Replace
20 | 4 | Newer than | 2019 | 12 | to | 2011 | 17 | to | 2006 | 20 | to | 2003
25 | 5 | Newer than | 2018 | 15 | to | 2008 | 21.25 | to | 2002 | 25 | to | 1998
30 | 6 | Newer than | 2017 | 18 | to | 2005 | 25.5 | to | 1998 | 30 | to | 1993
35 | 7 | Newer than | 2016 | 21 | to | 2002 | 29.75 | to | 1993 | 35 | to | 1988
40 | 8 | Newer than | 2015 | 24 | to | 1999 | 34 | to | 1989 | 40 | to | 1983
45 | 9 | Newer than | 2014 | 27 | to | 1996 | 38.25 | to | 1985 | 45 | to | 1978
50 | 10 | Newer than | 2013 | 30 | to | 1993 | 42.5 | to | 1981 | 50 | to | 1973
55 | 11 | Newer than | 2012 | 33 | to | 1990 | 46.75 | to | 1976 | 55 | to | 1968
60 | 12 | Newer than | 2011 | 36 | to | 1987 | 51 | to | 1972 | 60 | to | 1963
65 | 13 | Newer than | 2010 | 39 | to | 1984 | 55.25 | to | 1968 | 65 | to | 1958
70 | 14 | Newer than | 2009 | 42 | to | 1981 | 59.5 | to | 1964 | 70 | to | 1953
75 | 15 | Newer than | 2008 | 45 | to | 1978 | 63.75 | to | 1959 | 75 | to | 1948
80 | 16 | Newer than | 2007 | 48 | to | 1975 | 68 | to | 1955 | 80 | to | 1943

## Useful Life
Typical Useful Life for Infrastructure Assets
Water | Useful Life Guideline | MY Schedule | Water | Useful Life Guideline | MY Schedule
Aerator | 20-25 |  | Membrane Treatment (reverse osmosis, microfiltration, ultra-filtration) | 7-10
Alarm System | 7-10 |  | Meter Reading Equipment | 10-15
Backflow Preventors | 20-30 |  | Meters - Master | 30-40
Backwash Tank/Reclaim Tank | 40-50 |  | Meters - Residential | 15-25
Blower | 15-20 |  | Mixer/Recirculation Pump | 5-10
Booster Station Pumps | 15-20 |  | Other Water Treatment (cartridge filter housing, softeners, etc.) | 10-20
Chemical Feed Pumps | 8-12 |  | Pumping Station | 40-50
Chemical Scale | 15-20 |  | Rotometer | 5-15
Chemical Storage Tank | 15-20 |  | SCADA System | 5-20
Computer | 5-8 |  | Service Line | 40-50
Control Panel | 10-20 |  | Storage Tank - Plastic (chemical tanks) | 20-25
Curb Stops | 40-50 |  | Storage Tank - Plastic (finished water) | 30-40
Dehumidifier | 10-15 |  | Storage Tank (bladder) | 5-7
Detention Tank (poured or package) | 30-40 |  | Storage Tank (exterior/interior paint) | 15-20
Distribution Lines | 70-80 |  | Storage Tank (hydropneumatic or air-over-water) | 40-60
Electrical Controls | 20-40 |  | Storage Tank (tower, ground storage, etc.) | 60-70
Electric Motors | 15-20 |  | Structure (Block) | 60-70
Filter - Concrete | 30-40 |  | Structure (Stick-built) | 30-40
Filter Media | 15-20 |  | Submersible Pumps | 7-10
Filter - Metal | 15-20 |  | Transducer | 10-20
Gas Detection Equipment | 5-10 |  | Treatment Plant Pumps (backwash, reclaim, booster, recirculation, mixer, etc.) | 15-20
Generator | 20-30 |  | Valves (electrical actuated) | 15-25
Heater - Electric | 5-15 |  | Valves (mechanical) | 35-40
Heater - Furnace | 15-20 |  | Valves (pneumatic) | 15-25
Hydrants (Flushing or Fire) | 40-60 |  | Vertical Turbine Pumps | 10-15
Laboratory Equipment | 10-15 |  | Wells | 40-60
Additional Items to Consider:
Include all equipment associated with the drinking water system.
The above useful life ranges are adequate if routine maintenance is performed on the equipment.
If routine maintenance is not performed, reduce the years of useful life ranges above. Lack of routine maintenance decreases the useful life of the equipment.

## Key Financial Indicator
KEY FINANCIAL INDICATORS
EXAMPLE
KEY
| 1 | Operating Revenue |  |  |  |  | 709972
| 2 | Operating Expenses (Including Depreciation) |  |  |  |  | 671333
| 3 | Operating Expenses (Excluding Depreciation) |  |  |  |  | 212251
| 4 | Principal & Interest on Long-Term Debt |  |  |  |  | 190633
| 5 | Unrestricted Cash & Cash Equivalents |  |  |  |  | 568061
| 6 | Receivables, net |  |  |  |  | 66346
| 7 | Current Liabilities |  |  |  |  | 898474
1. Operating Ratio
-Operating ratio measures self-sufficiency. The revenue you get
from daily operations, divided by the expenditures or expenses
you make to keep operations running.
Natural Benchmark: > 1.0; higher preferred
709972
Operating Revenues (1)
1a. |  |  |  |  | = | 1.0576
671333
Operating Expenses
(including depreciation) (2)
709972
Operating Revenues (1)
1b. |  |  |  |  | = | 1.5465
459082
Operating Expenses
(excluding depreciation) (2-3)
2. Debt Service Coverage Ratio
-A measure of the ability to pay debt service with operating revenue
Natural Benchmark: > 1.0; though funders often set requirements above 1.0 (usually > 1.2)
|  | 709972 | - |  | 459082
|  | Operating Revenues (1) |  | Operating Expenses
(excluding depreciation) (2-3)
2. | [7 empty] | = | 1.3161
190633
Principal & Interest on Long-Term Debt (4)
3. Current Ratio
-A measure of short-term liquidity: ability to pay your current bills
Natural Benchmark: > 1.0; > 2.0 is preferred
Link to
|  | 568061 | + |  | 66346 |  |  |  |  | WEBINAR (Minnesota)
|  | Unrestricted Cash & |  | Receivables, net (6) | [5 empty] | Financial Management for
|  | Cash Equivalents (5) | [7 empty] | Water and Wastewater Funding
3. | [7 empty] | = | 0.70609 | Program Applications
in Minnesota
|  | 898474 | [7 empty] | Below:
Current Liabilities (7)
WEBINAR (Minnesota) ¦ Financial Management for Water and Wastewater Funding Program Applicants in Minnesota - Environmental Finance Center Network (efcnetwork.org)

## Rate Sheet
ANNUAL RATE SHEET
CITY OF
| POPULATION |  |  |  | MINNESOTA RURAL WATER ASSN
| NUMBER OF CONNECTIONS |  |  |  | 217 12th AVENUE SE
| AVE PERSONS/CONNECTION |  | #DIV/0! |  | ELBOW LAKE, MN 56531
800-367-6792
| EXPENSES (PER YEAR) |  |  |  | Web: www.mrwa.com
SALARIES
FRINGE BENEFITS
ELECTRICITY/HEATING
SUPPLIES
MILEAGE/POSTAGE/GAS
REPAIRS/MAINTENANCE
BUILDING REPAIRS
TESTS
CONTRACTUAL
PROFESSIONAL MEMBERSHIPS
| PRINTING/PUBLISHING |  |  |  | Name of person filling out this form:
PERMIT FEES
| SUBSCRIPTIONS |  |  |  | _____________________________________
CHEMICALS
| TRAINING EXPENSE |  |  |  | Telephone Number:
CAPITAL OUTLAY
| BOND & INTEREST |  |  |  | _____________________________________
DEPRECIATION
| OTHER | MISCELLANEOUS
| EXISTING AND FUTURE DEBT | INSURANCE |  |  | PLEASE FILL IN LINE ITEMS WITH THIS SHADING
| ASSET RESERVE |  |  |  | ALL OTHER CALCULATIONS WILL BE MADE AUTOMATICALLY
OPERATING EXPENSE
OTHER
| TOTAL EXPENSE |  | 0
WATER USAGE (GALLONS SOLD LAST YEAR)
WATER USAGE (GALLONS PUMPED LAST YEAR)
| UNACCOUNTED FOR WATER |  |  | 0 | #DIV/0! | unbilled/unaccounted for water
| WATER USE PER CONNECTION |  |  | #DIV/0!
| WATER USE PER CONNECTION/DAY |  |  | #DIV/0!
| COST TO PRODUCE A THOUSAND GALLONS |  |  | #DIV/0!
| USAGE PER PERSON PER DAY |  |  | #DIV/0!
|  |  | ENTER HERE |  |  | Yearly Total
|  | Your Base Rate |  | 0 |  | 0
|  | Your Gallon Included | 0 | 0 |  | 0
Your Billing Cycle*
|  | *Billing Cycle examples: Monthly = 12; Quarterly = 4; etc. |  |  | If you increase your base rate:
[5 empty] | 25% | 50% | 75%
| YEARLY BASE RATE |  |  | 0 | 0 | 0 | 0
| FOR HOW MANY GALLONS |  |  | 0 | 0 | 0 | 0
| ADDITIONAL YEARLY INCOME REQUIRED |  |  | 0 | 0 | 0 | 0
| GALLON SALES REQUIRED TO BREAK EVEN |  |  | 0 | 0 | 0 | 0
| RATE PER THOUSAND GALLONS |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
IF THE EXPENSE REPORT LINE ITEMS ARE NOT THE SAME AS YOUR SYSTEM USES, FEEL FREE TO CHANGE THEM
COMMENTS:

## SWP Questions
Source Water Protection Questions
| No. |  | *For ANSWER, please select from the drop down options of "Yes," "No," or "Not Sure." | Answer
| 1 | Has drought impacted the water level in your wells or caused supply shortages? |  | Yes
| 2 | Are your wells located in areas prone to flooding or areas that pond precipitation or runoff for extended periods of time? |  | Yes
| 3 | Are your wells located near a roadway or railroad tracks where an accident could cause a spill that may threaten your water supply? |  | Yes
| 4 | Are you aware of how to contact spill response assistance in the event of a hazardous materials spill? |  | Yes
| 5 | Is your water system emergency response plan periodically reviewed, updated and available in the event of an emergency? |  | Yes
| 6 | Does your water system own or have long-term leases on the 50 foot area surrounding your wells? |  | Yes
| 7 | Are your wells located within 100 feet of cropland or row crop agriculture? |  | Yes
| 8 | Are your wells located within 100 feet of livestock, pasture or feeding areas? |  | Yes
| 9 | Are there any above or below ground fuel oil, gasoline, farm chemical or other large storage tanks located within 200 feet of your wells? |  | Yes
| 10 | Are there any large manufacturing or processing facilities within 200 feet of your wells that may have chemicals that could impact your wells? |  | Yes
| 11 | Do any petroleum pipelines run within 200 feet of your wells or underground water storage facilities? |  | Yes
| 12 | Are the locations of sanitary and storm sewer lines identified within 200 feet of your wells? |  | Yes
|  | 12a. | Are the sanitary sewer lines in good condition? | Yes
|  | 12b. | Are the sanitary sewer lines inspected regulary? | Yes
|  | 12c. | Are the storm sewer lines in good condition? | Yes
|  | 12d. | Do the storm sewer lines require inspection and maintenance? | Yes
| 13 | Is backup power available and adequate to assure your wells continue to function and avoid a water system depressurization or well backflow condition? |  | Yes
| 14 | Are your wells protected from physical damage caused by cars, mowers or other mobile equipment that may accidentally collide with the well casings? |  | Yes
| 15 | Are your wells, water plant and water storage facilities secure from vandalism or tampering? |  | Yes
| 16 | Would installation of fencing, alarm system or security cameras be useful to your system? |  | Yes
| 17 | Do your well logs and well maintenance records give you an accurate understanding of your well condition? |  | Yes
| 18 | Would televising your wells or other Minnesota Department of Health well characterization testing help you determine your well’s physical condition? |  | Yes
Any "yes" answers above may result in new funding opportunities for the system to improve drinking water infrastructure assests that will protect drinking water
resources thru Federal or State Grants. For more information, please contact your MDH/MRWA Source Water Protection (SWP) Planner for assistance.
https://www.mrwa.com/financing/mn-loan-and-grant-funding-options/
MDH SWP Contacts |  |  | https://www.health.state.mn.us/communities/environment/water/docs/swpstaffmap.pdf
MRWA SW Maps |  |  | https://www.mrwa.com/PDF/MRWA%20SWP%20Staff%20Work%20Areas%202019.pdf
MRWA Staff Info |  |  | https://www.mrwa.com/staff/
MRWA Office Toll Free Number 800-367-6792